ABB Bailey INFI 90 Migration Studio

1. Introduction

ABB Bailey INFI 90 Migration Studio is intended to be a migration-analysis and engineering reconstruction platform for legacy Bailey INFI 90 DCS backup data. The platform will accept a Bus/Module backup package as a ZIP input, automatically identify and classify the different legacy engineering file types contained within the package, extract and correlate engineering information, reconstruct the relationship between I/O, logic, configuration and operator graphics, and present the resulting engineering information through structured outputs and an integrated viewer.

The platform is therefore not limited to a conventional data-extraction or Excel-generation utility. It is intended to function as an engineering intelligence, reconstruction, mapping and visualization environment for Bailey INFI 90 migration activities.

The supplied M5 archive was analyzed as the reference input package. It contains 293 ZIP entries, of which 292 are data files and one is the M5 directory entry. The archive contains 243 CAD files, 30 M1 files, 1 OUT file, 1 REF file, 1 XRF file, 1 ERR file, 2 CFG files, 1 VFY file, 1 MHD file, 3 LST files, 3 LOG files, 1 MDC file, 1 GES file, 1 BND file and 2 BAT files. The XRF processing log independently records that 243 CAD sheets were processed, confirming the CAD population present in the example package.

The M5 package is to be treated strictly as an example of the input structure and file ecosystem. Future project inputs may contain different loop numbers, CPU/PCU numbers, module numbers, CAD sheet names, tags, descriptions, graphics and file populations. The platform must therefore be designed around file type, content structure and engineering relationships rather than hard-coded filenames or project-specific identifiers.

2. Input System Structure

The source environment follows the hierarchical structure:

DCS System → Bailey INFI 90 → Loop/Network → CPU/PCU → Bus/Module

For example:

- Loop: L1, L2, L3

- CPU / PCU: P1, P2, P3

- Bus / Module: M1, M2, M3

- Module ZIP: Contains the complete collection of legacy files associated with the selected Bus/Module.

A representative source path may therefore be expressed as:

D:\PROJECT\L2\P12\M5\

The ZIP uploaded to the platform represents the contents of the M5 Bus/Module level, not the complete DCS system.

The platform must preserve the source hierarchy as project metadata so that every extracted object can remain traceable to its originating:

- Loop

- CPU / PCU

- Bus / Module

- Source filename

- Source file type

- CAD sheet or graphic

- Original engineering reference

This provenance is essential because the same device, tag or function may occur across multiple CAD sheets and graphics.

3. Reference Output Material

Two supplied reference PDFs establish the expected visual representation of the generated outputs.

The CAD reference PDF contains 288 pages of rendered Bailey engineering sheets. The pages demonstrate that the source CAD information includes engineering drawings, function blocks, I/O references, block identities, signal references, descriptions, interconnections and engineering text. Individual sheets contain structures such as S1, S2, function-code identifiers, block numbers, AI/AO/DI/DO references and cross-sheet references.

The CAD material also demonstrates that the engineering information is not restricted to simple I/O lists. Function blocks such as sequence, timer, PID, arithmetic and other Bailey function codes occur within the logic sheets, together with their signal references and specifications. Examples include function-code references such as PID, ETIMER, DSUM, SEQMON, SEQGEN, REMSET and associated S1, S2, S3 and subsequent specification fields.

The Graphics reference PDF contains 82 pages and demonstrates the expected M1 visualization representation. It contains original graphics as well as corresponding versions with marking tags. The graphics include operator displays, menus, process diagrams, equipment symbols, measurements, alarms, states and engineering tags.

The output representation must therefore preserve the engineering appearance of the original CAD and M1 material, rather than converting everything into only tabular text.

4. Input File Classification

The ZIP ingestion engine shall first perform complete file discovery and classification before engineering extraction begins.

The M5 reference package establishes the following file ecosystem.

4.1 .CAD — Engineering and Logic Sheets

The .CAD files are the primary engineering source for control logic reconstruction.

The reference specification states that CAD sheets contain:

- Function-block logic

- I/O references

- Interconnections

- Block identities

- Descriptions

- Source references

- Destination references

- Engineering text

- Logic structure

- Function-code specifications

The platform shall therefore use .CAD files as the primary source for:

- AI identification

- AO identification

- DI identification

- DO identification

- Loop-tag extraction

- Device references

- Function-block identification

- Block IDs

- Function codes

- S0–S9 specifications

- Logic/formula information

- Input references

- Output references

- Cross-sheet references

- Descriptions

- Engineering annotations

- CAD sheet reconstruction

The reference documentation explicitly identifies CAD as the primary source for DCS logic reconstruction and as the source for the CAD PDF/viewer representation.

The example M5 ZIP contains 243 CAD files.

The platform must inspect all CAD files, not only those containing conventional I/O. The reference archive demonstrates that CAD sheets may contain physical I/O, control logic, function blocks, sequences, timers, interconnections and supporting engineering information.

A CAD sheet may therefore be classified according to its detected engineering content rather than by filename alone.

4.2 .M1 — Operator Graphics

.M1 files represent the Bailey graphic/model environment.

The supplied specification identifies M1 files as containing:

- Graphical objects

- Models

- Tags

- Text

- Buttons

- References

- Graphic indices

- Display components

The M1 subsystem is therefore the primary source for operator-facing graphics.

The reference archive contains 30 M1 files.

These include graphics represented by naming groups such as:

- 322P01.m1

- 322PL01.m1 through 322PL13.m1

- 322PML01.m1

- 322PMQ01.m1

- 322PMS01.m1

- 322PMT01.m1

- 322PS01.m1 through 322PS04.m1

- 322PT01.m1 through 322PT08.m1

The platform shall extract sufficient M1 information to:

- Identify the graphic

- Identify graphical objects

- Identify associated tags

- Identify text and descriptions

- Identify displayed engineering references

- Maintain tag-to-graphic relationships

- Maintain relationships between graphics and engineering tags

- Generate the M1 graphic representation as PDF

- Make the graphic available within the viewer

The supplied Graphics reference confirms that the expected output includes both the original graphic representation and engineering-tag-marked representation.

4.3 .OUT — I/O and Cross-Reference Information

I90XREF.OUT is the primary source for cross-sheet signal mapping.

It contains:

- CAD sheet sections

- Outputs

- Inputs

- Descriptions

- Source points

- Destination points

- Destination CAD sheets

The reference specification explicitly defines .OUT as the primary cross-sheet mapping source.

The M5 example contains 241 CAD output sections and 241 CAD input sections in the human-readable cross-reference report.

The platform shall preserve the original OUT data and extract the engineering I/O representation required for the final mapping.

The required I/O scope is strictly:

- AI — Analog Input

- AO — Analog Output

- DI — Digital Input

- DO — Digital Output

The platform shall parse the original I/O structure without destroying the raw source value.

A representative record such as:

DO5-40B/282MCR-M360

shall be interpreted as:

- I/O Type: DO

- Channel: 5

- Slave: 40B

- Device Tag: 282MCR-M360

- Raw I/O Tag: DO5-40B/282MCR-M360

The raw value shall always remain available for traceability.

4.4 .REF — Reference and Tag Database

The .REF file provides a module-level engineering reference/tag database.

Examples in the supplied material include references such as:

DI1-1A/322AUX-M107A

AI6-8/322LT-654

The .REF file shall be used as a reference and validation layer, not as the sole source of I/O truth.

Its primary functions are:

- Tag normalization

- Signal validation

- Reference enrichment

- Detection of engineering tags

- Cross-checking CAD and OUT records

- Supporting the master engineering tag database

4.5 .XRF — Processing and CAD Coverage Validation

I90XREF.XRF is a processing log associated with the cross-reference generation.

The example explicitly records:

No. of CAD Sheets to Process = 243

and identifies each CAD sheet as it is read. It also records conditions such as blank descriptions.

The platform shall use .XRF to establish:

- Expected CAD count

- Processed CAD count

- Sheet processing coverage

- Processing warnings

- Blank-description conditions

- Ingestion completeness

.XRF is a validation/diagnostic source rather than the main engineering extraction source.

4.6 .ERR — Unresolved Engineering References

I90XREF.ERR contains unresolved output/reference records and their originating CAD locations.

The example contains unresolved records such as digital signals and engineering device references linked to specific CAD sheets.

The platform shall not silently discard unresolved records.

Each unresolved record shall become a validation item with information such as:

- Raw unresolved reference

- Source CAD point

- Source CAD file

- Reference type

- Resolution status

- Possible matching candidates

- Final mapping state

The reference material explicitly identifies .ERR as useful for a viewer validation/error panel and requires unresolved links to remain visible.

4.7 .CFG — Configuration and Function-Block Data

The .CFG files contain binary configuration information for the Bailey module.

The reference material defines them as containing module/function-block configuration and identifies them as a source for:

- Configuration-level function-block data

- Block validation

- Function-code specifications

- Potential S1/S2/... data

The CAD logic and configured function blocks must ultimately correlate with this configuration data.

The example package contains:

- 30705.CFG

- CONFIG.CFG

30705.CFG represents the module/source configuration, while CONFIG.CFG is used as the comparison/reference configuration within the supplied verification material.

4.8 .VFY — Configuration Verification

30705.VFY is a verification report comparing source and reference configuration.

The example explicitly identifies:

- Loop 3

- PCU 7

- Module 5

- Source CFG

- Reference CFG

and reports configuration block totals and verification status. The supplied VFY example reports 2,782 source blocks and 2,782 reference blocks with no differences detected during that verification operation.

The platform shall use VFY to:

- Validate configuration consistency

- Validate block population

- Identify specification differences where present

- Support engineering verification

- Expose configuration mismatches in the validation interface

4.9 .MHD — Module Header Information

The .MHD file contains module-level identity information.

The example identifies information such as:

- Module type

- Module identity

- MFP02

The platform shall use this file to enrich module metadata and establish the module-level identity associated with the backup.

4.10 .LST — Project and Sheet Index

The .LST files act as project/module indexes.

The reference material identifies:

- 30705.LST — CAD sheet list

- MSTR.LST — module identification

- SELCT.LST — selected project path

The platform shall use these files to identify:

- Module identity

- CAD population

- Project provenance

- Expected engineering inventory

The LST information should be cross-validated against the physical ZIP contents.

4.11 .LOG — Processing History

The archive contains:

- 30705.LOG

- CADSYNC.LOG

- UNTITLED.LOG

These files contain processing history, CAD synchronization information, script/verification activity and configuration differences.

They shall be used for:

- Processing audit

- Diagnostics

- Debugging

- Coverage checking

- Warning reporting

- Verification history

- Processing status

They are supporting files, not primary engineering extraction sources.

4.12 .MDC — Source Provenance

The .MDC file contains a reference to the original Bailey project/module environment.

The platform shall retain this information as:

- Source provenance

- Original project location

- Backup origin metadata

- Engineering traceability

It is not a primary I/O or logic extraction source.

4.13 .GES — Legacy Resource Data

The .GES file is legacy/global string/resource information.

The supplied archive does not establish it as a standalone engineering table. Therefore, the initial implementation should:

- Preserve the file

- Associate it with the project

- Make it available to the graphics subsystem

- Parse it only when required for graphics/resource rendering

The supplied specification specifically identifies it as potentially relevant to legacy graphics/configuration resources.

4.14 .BND — Supporting Engineering Metadata

The .BND file contains module-associated engineering text and tags.

Examples include:

- WOODYARD POWER CONSUMTION

- 411FI-0205

- Other engineering references

It should be treated as a supporting enrichment source and correlated with CAD, REF and M1 information wherever common tags exist.

4.15 .BAT — Legacy Processing Commands

The archive contains:

- M5.bat

- P7.bat

These are legacy batch/automation commands associated with the old Bailey project environment.

They are not primary engineering data sources. They should therefore be:

- Preserved

- Catalogued

- Associated with source provenance

- Available for engineering audit

- Excluded from primary logic/I/O extraction unless a future migration requirement explicitly requires them

The supplied reference documentation categorizes these files as process/provenance information.

5. Core Processing Logic

The platform shall follow a content-driven extraction strategy.

The uploaded ZIP must first be treated as an unknown Bus/Module backup rather than as a known M5 project.

The first processing operation shall establish:

- Archive validity

- Directory structure

- File inventory

- File extensions

- File counts

- File sizes

- File encoding/format

- Binary versus text classification

- Duplicate files

- Missing expected file classes

- Unexpected file classes

The system shall then construct a Module Data Inventory containing every discovered file and its role.

The file inventory shall become the foundation for all subsequent extraction and validation operations.

No individual file should be analyzed in isolation when its content is dependent on another source.

For example:

- .OUT provides I/O/device references.

- .CAD provides the engineering context and associated loop information.

- .REF validates and enriches tags.

- .LST establishes the CAD inventory.

- .XRF validates CAD processing coverage.

- .ERR identifies unresolved relationships.

- .CFG provides configuration-level block information.

- .VFY provides configuration validation.

- .M1 provides operator graphics.

- .BND provides supporting engineering metadata.

The platform must therefore establish a common engineering data model in which these independent legacy files become linked entities.

6. CAD Processing Logic

Each CAD file shall be processed as an individual engineering sheet while simultaneously being associated with the complete module.

For every CAD file, the engine shall identify:

- CAD filename

- Sheet identifier

- Sheet title where available

- Drawing description

- Engineering descriptions

- Loop tags

- Device tags

- I/O references

- Block IDs

- Function codes

- Block specifications

- S0

- S0.5

- S1

- S2

- S3

- S4

- S5

- S6

- S7

- S8

- S9

- Input references

- Output references

- Source references

- Destination references

- Cross-sheet references

- Engineering text

- Logic/formula information

The reference CAD material shows that block-level information can occur in structures containing function-code identifiers and specification terminals such as S1, S2, S3 and subsequent specification parameters.

The extraction engine must not assume that every function block uses every specification field. Missing fields must remain explicitly empty rather than being inferred.

Likewise, the engine must distinguish between:

- A numeric block identifier

- A function code

- An I/O reference

- A physical device tag

- A loop tag

- A cross-sheet reference

- A textual description

These are different engineering entities and must not be merged into a single unstructured field.

7. Function-Code and S1–S9 Extraction

The function-code extraction subsystem is a central requirement.

The supplied Logic Specification Extraction Template defines the expected structure:

- CAD File

- Loop Tag

- Description

- Block ID

- Function Code

- S0

- S0.5

- S1

- S2

- S3

- S4

- S5

- S6

- S7

- S8

- S9

- Logic / Formula

- Input Reference(s)

- Output Reference(s)

- Device Tag

- Notes

The template explicitly defines the S0–S9 fields as function-code specification fields and identifies CAD/configuration as their source.

The platform shall therefore create a Function Block Record for each uniquely identifiable function block.

Each record shall retain:

Block Identity → Function Code → Specifications → Inputs → Outputs → Logic Interpretation → Engineering Context

Where a detailed function specification exists elsewhere in the ZIP, the engine shall locate and associate that information with the originating block.

The platform must therefore support multi-file function specification resolution, rather than assuming that every specification is completely contained on the visible CAD sheet.

The .CFG subsystem shall participate in this process because the reference material identifies configuration as a potential source for encoded S1/S2/... function specifications.

8. Logic / Formula Representation

The platform shall retain both:

- The original engineering representation, and

- A normalized human-readable representation

The original representation is required for traceability and viewer inspection.

The normalized representation shall provide a readable interpretation of the function block where the data supports such interpretation.

Examples of engineering function structures visible in the CAD material include:

- PID

- ETIMER

- DSUM

- SEQMON

- SEQGEN

- REMSET

- TD-DIG

- Logic gates such as NOT and OR

- Arithmetic and comparison-related blocks

- State/sequence-related structures

The CAD reference contains examples where function blocks have explicit specifications and numbered signal references, demonstrating that the logic data is structured around block/function relationships rather than only free-form drawing text.

The resulting logic record shall therefore be suitable for migration engineering review and downstream conversion rather than being merely a text transcription.

9. I/O Extraction and Mapping Logic

The platform shall focus on the four required I/O classes:

AI, AO, DI and DO

The .OUT parser shall first extract:

- I/O Type

- Channel

- Slave

- Device Tag

- Raw I/O Tag

The supplied Loop Tag Mapping Template defines this extraction explicitly and states that:

- I/O Type comes from .OUT

- Channel comes from .OUT

- Slave comes from .OUT

- Device Tag comes from .OUT

- Raw I/O Tag comes from .OUT

- Loop Tag comes from .CAD

- Description comes from .CAD

- CAD File comes from .CAD

- Final mapping is produced using .OUT + .CAD.

The final mapping model shall therefore be:

OUT Device Reference → CAD Engineering Context → Loop Tag → Description → CAD File

The mapping engine shall retain:

- Raw source I/O

- Parsed I/O type

- Channel

- Slave

- Device tag

- Matched CAD file

- Loop tag

- Description

- Mapping status

- Validation notes

10. Loop Tag Extraction

The Loop Tag is not to be assumed to be identical to the Device Tag.

The Loop Tag shall be extracted from the relevant CAD engineering content and associated with the corresponding .OUT record through an engineering-reference matching mechanism.

The matching engine shall use multiple available indicators where necessary, including:

- Device tag

- I/O reference

- CAD file

- Source reference

- Destination reference

- Engineering text

- .REF validation

- .OUT source/destination information

- Cross-sheet references

A successful mapping shall therefore identify not only the I/O record but also where that signal exists in the control logic.

This is a key requirement because the purpose is not simply to generate an I/O inventory; it is to establish the engineering relationship between physical I/O, process loop, device, control logic and CAD sheet.

11. Description Extraction

Descriptions shall be collected from the highest-confidence engineering source available.

Primary description sources shall include:

- CAD engineering text

- CAD sheet descriptions

- OUT descriptions

- M1 displayed text

- BND metadata

- REF information where appropriate

The system shall preserve the source of the description so that users can distinguish:

- CAD-derived description

- OUT-derived description

- Graphics-derived description

- Enriched description

- Missing description

Blank descriptions must not be converted into fabricated values.

The XRF reference specifically demonstrates that blank descriptions can occur in real engineering data, making explicit missing-data handling necessary.

12. Cross-Sheet Relationship Processing

The platform shall build a structured relationship between CAD sheets.

The .OUT report provides the source and destination relationship required for this purpose.

For each signal, the system should be able to determine:

- Source CAD sheet

- Source reference

- Source description

- Destination CAD sheet(s)

- Destination reference(s)

- Related block

- Related I/O

- Related loop tag

- Related device tag

The reference specification explicitly identifies this as the critical mechanism for building the relationship between CAD sheets.

This relationship must be stored as reusable engineering data so that the Viewer can navigate from one related object to another.

13. M1 Graphics Processing Logic

The M1 subsystem shall separately process the graphics environment.

For every M1 file the engine shall identify:

- Graphic identifier

- Graphic name

- Graphic objects

- Object type

- Display text

- Engineering tags

- Buttons

- References

- Graphic indices

- Associated resources

- Tag relationships

The system shall preserve the actual graphical appearance and generate the required M1 Graphics PDF.

The supplied graphics reference demonstrates that a single graphic may contain multiple process sections, equipment elements, buttons, engineering values, alarms and tags, and that the marked version overlays engineering tags onto the same operator graphic.

The platform shall therefore support both:

Original Graphics Representation

and

Engineering-Marked Graphics Representation

where the required tag information can be resolved.

14. PDF Generation Requirements

14.1 CAD PDF

The CAD subsystem shall produce a PDF representation containing the complete rendered logic/engineering sheets.

The generated PDF must preserve:

- Sheet boundaries

- Drawing content

- Function blocks

- Lines/connections

- Engineering text

- I/O references

- Block identifiers

- Descriptions

- Original sheet sequence

- Sheet identity

- Visual engineering context

The intended result corresponds to the supplied CAD reference PDF, which contains the rendered engineering sheets rather than merely extracted text.

14.2 M1 Graphics PDF

The graphics subsystem shall generate PDF representations of the M1 graphics while preserving:

- Original display composition

- Text

- Graphics

- Symbols

- Equipment representation

- Engineering tags

- Navigation/interface elements

- Display hierarchy

The supplied Graphics reference demonstrates the expected visual presentation.

15. Integrated Engineering Viewer

The final platform shall contain an integrated viewer rather than functioning only as a document generator.

The viewer shall provide access to:

- CAD sheets

- M1 graphics

- I/O records

- Loop tags

- Device tags

- Function blocks

- Function codes

- S0–S9 specifications

- Logic/formula information

- Cross-sheet references

- Descriptions

- Validation results

- Unresolved links

- Configuration verification information

A user shall be able to inspect a CAD sheet and identify the associated engineering information without leaving the platform.

Likewise, an I/O record should provide access to its associated:

- Device tag

- Loop tag

- Description

- CAD sheet

- Logic context

- Related signals

- Related graphics where a matching engineering tag exists

An M1 graphic should similarly provide its associated engineering references wherever those references can be resolved.

This transforms the platform from an extraction system into an engineering navigation and reconstruction environment.

16. Master Engineering Data Model

The platform should maintain a normalized internal representation with the following primary entities:

Project Entity

- Project ID

- Source ZIP

- Loop

- CPU / PCU

- Bus / Module

- Source path

- Processing timestamp

- File inventory

- Processing status

CAD Sheet Entity

- CAD File

- Sheet ID

- Description

- Engineering text

- Loop tags

- Device tags

- I/O references

- Function blocks

- Cross-sheet references

- Rendered PDF reference

Function Block Entity

- Block ID

- Function Code

- S0

- S0.5

- S1

- S2

- S3

- S4

- S5

- S6

- S7

- S8

- S9

- Logic / Formula

- Input References

- Output References

- CAD File

- Device Tag

- Notes

I/O Entity

- I/O Type

- Channel

- Slave

- Device Tag

- Raw I/O Tag

- Loop Tag

- Description

- CAD File

- Source reference

- Destination reference

- Mapping status

Graphic Entity

- M1 File

- Graphic ID

- Object information

- Text

- Engineering tags

- References

- Rendered graphic PDF

- Related CAD/I/O records

Validation Entity

- Validation type

- Source file

- Source object

- Error/warning

- Resolution status

- Related CAD file

- Related I/O

- Related reference

17. Algorithm Requirements

The extraction engine shall use a layered approach.

Layer 1 — Archive Intelligence

- Validate ZIP

- Enumerate all files

- Identify extensions

- Identify file formats

- Record file metadata

- Establish module inventory

Layer 2 — File-Type Parsing

- Parse CAD

- Parse M1

- Parse OUT

- Parse REF

- Parse XRF

- Parse ERR

- Parse CFG

- Parse VFY

- Parse LST

- Parse LOG

- Parse MHD

- Parse MDC

- Parse BND

- Preserve GES

- Preserve BAT

Layer 3 — Engineering Entity Extraction

Extract:

- I/O

- Tags

- Loop tags

- Descriptions

- CAD sheets

- Function blocks

- Function codes

- S0–S9

- Logic/formulas

- Inputs

- Outputs

- Sources

- Destinations

- Graphics

Layer 4 — Correlation

Correlate:

- OUT ↔ CAD

- CAD ↔ REF

- CAD ↔ CFG

- CFG ↔ VFY

- CAD ↔ M1

- CAD ↔ OUT

- CAD ↔ ERR

- CAD ↔ XRF

- CAD ↔ BND

Layer 5 — Validation

Validate:

- File completeness

- CAD count

- Sheet processing count

- Missing descriptions

- Missing mappings

- Unresolved references

- Duplicate identifiers

- Configuration differences

- Orphaned I/O

- Orphaned graphics

- Broken cross-sheet references

Layer 6 — Rendering

Generate:

- CAD PDF

- M1 Graphics PDF

- Viewer-ready CAD representation

- Viewer-ready graphics representation

Layer 7 — Structured Output

Generate:

- I/O Mapping

- Logic Specification Extraction

- Engineering Tag Database

- Cross-Sheet Relationships

- Validation Records

- Provenance metadata

18. Required Output — I/O Mapping

The final I/O mapping shall follow the structure defined by the supplied template:

| Field | Required Source |
| --- | --- |
| I/O Type | .OUT |
| Channel | .OUT |
| Slave | .OUT |
| Device Tag | .OUT |
| Loop Tag | .CAD |
| Description | .CAD / enriched source |
| CAD File | .CAD |
| Raw I/O Tag | .OUT |

The mapping template explicitly defines this structure and identifies the final mapping as an .OUT + .CAD correlation.

19. Required Output — Logic Specification

The final logic specification shall contain:

- CAD File

- Loop Tag

- Description

- Block ID

- Function Code

- S0

- S0.5

- S1

- S2

- S3

- S4

- S5

- S6

- S7

- S8

- S9

- Logic / Formula

- Input Reference(s)

- Output Reference(s)

- Device Tag

- Notes

This exactly follows the supplied Logic Specification Extraction Template and its column definitions.

The output shall distinguish between:

- Directly extracted values

- Configuration-derived values

- Cross-referenced values

- Inferred/normalized values

- Missing values

- Validation warnings

20. Required Output — CAD Logic PDF

The platform shall generate a complete CAD PDF representing the available CAD engineering sheets.

The output shall support:

- Sheet-level identification

- Original drawing appearance

- Complete logic representation

- I/O representation

- Function-block representation

- Engineering descriptions

- Cross-sheet references

The PDF shall remain linked to the internal CAD Sheet Entity so that selecting a sheet in the viewer can open the corresponding rendered engineering representation.

21. Required Output — M1 Graphics PDF

The platform shall produce the corresponding graphics PDF for the M1 dataset.

The output shall contain the rendered operator graphics and maintain links to the extracted M1 objects and engineering tags.

The graphics output shall support engineering review independently while remaining connected to the common engineering database.

22. Required Output — Viewer

The final Viewer shall provide a unified engineering inspection environment containing:

CAD Viewer

- CAD sheet list

- CAD sheet search

- Full-sheet rendering

- Zoom

- Pan

- Engineering text access

- Function block identification

- I/O highlighting

- Block selection

- Cross-sheet navigation

Graphics Viewer

- M1 graphic list

- Full graphic rendering

- Engineering tag display

- Tag lookup

- Graphic object information

- Related engineering information

Engineering Data Viewer

- I/O list

- Loop Tag

- Device Tag

- Description

- CAD File

- Function Block

- Function Code

- S0–S9

- Logic/formula

- Source/destination references

Validation Viewer

- Unresolved references

- Missing descriptions

- Missing mappings

- Processing warnings

- CAD coverage

- Configuration verification

- Cross-reference issues

23. Processing Engine

The core engine should be divided conceptually into specialized processing components:

Archive Processing Engine

Responsible for identifying and inventorying all uploaded files.

CAD Parsing Engine

Responsible for extracting logic, I/O, blocks, tags, descriptions, specifications and relationships.

M1 Graphics Parsing Engine

Responsible for extracting and reconstructing operator graphics.

Cross-Reference Engine

Responsible for processing OUT, XRF and ERR information and creating relationships between CAD sheets.

Configuration Engine

Responsible for processing CFG and VFY information.

Engineering Correlation Engine

Responsible for connecting:

- I/O

- CAD

- Function blocks

- Tags

- Loop tags

- Descriptions

- Graphics

- Configuration

Validation Engine

Responsible for identifying incomplete, inconsistent and unresolved engineering records.

Rendering Engine

Responsible for generating the CAD and M1 PDF representations and viewer-renderable assets.

Engineering Database

Responsible for storing normalized engineering entities and maintaining source-level provenance.

Viewer Engine

Responsible for presenting the reconstructed engineering environment to the end user.

24. Engineering Traceability Requirement

Every extracted engineering record shall remain traceable to its original source.

For example, an I/O record must be traceable through:

I/O Record → OUT Record → Device Tag → CAD File → Loop Tag → CAD Logic → Function Block → Related Graphic

Similarly, a function block must be traceable through:

Function Block → CAD Sheet → Function Code → S1–S9 → Input/Output References → Related CAD Sheets

This traceability is a fundamental requirement of the migration platform because the platform must support engineering verification rather than simply producing derived data.

25. Validation and Data Integrity

The system shall never treat extraction as successful merely because text was found.

Successful processing shall require validation of:

- Expected versus actual file counts

- CAD processing coverage

- CAD-to-LST consistency

- XRF processing coverage

- OUT-to-CAD mappings

- REF validation

- Function-block completeness

- CFG/VFY consistency

- Unresolved references

- Missing descriptions

- Missing loop tags

- Missing device tags

- Duplicate identifiers

- Orphaned records

The supplied M5 example already demonstrates that unresolved references and blank descriptions are real conditions in the source environment; therefore, incomplete engineering relationships must be represented explicitly rather than hidden.

26. Final Platform Objective

The final objective of ABB Bailey INFI 90 Migration Studio is to convert a legacy Bailey Bus/Module backup from a collection of disconnected legacy files into a searchable, traceable and visually reconstructed engineering dataset.

The platform shall produce four principal engineering outcomes:

CAD

Complete reconstructed CAD logic sheets in PDF and viewer format, including engineering logic, function blocks, I/O references, tags, descriptions and cross-sheet relationships.

Graphics

Complete M1 graphics in PDF and viewer format, preserving the operator-facing visual representation and associated engineering tags.

I/O List

A structured AI/AO/DI/DO mapping containing channel, slave, device tag, raw I/O reference, CAD file, loop tag and description.

Logic List

A structured function-block dataset containing block identity, function code, S0–S9 specifications, logic/formula, input references, output references, device tags and engineering notes.

The resulting platform shall therefore provide not only data extraction, but also engineering reconstruction, cross-reference intelligence, validation, traceability and interactive viewing of the Bailey INFI 90 system represented by the uploaded Bus/Module backup.